{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["Setpoint (holding)","Datapoint (input)"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":5,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Setpoint (holding)","index":0,"n_rows":154,"n_cols":15,"rows_kept":154,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,"Modbus setpoints P631","holding register","Microbooster\nFirmware 1.5\n18-05-2021"]
[null,"Modbus Code","Parameter","Read/Write (D02.4 Modbus modify = 0) ","Read/Write (D02.4 Modbus modify = 1) ","Data Type","Raw minimum value","Raw maximum value","Min value","Max Value","Format","Unit",null,"Comment","Page in manual"]
[null,"4x0000","P Mode (0=AUTO 1=ECO 2=BOOST 3=BACK-UP  4=HOLIDAY)","R","R/W","uint16",0,4,0,4,"*1"," ",null,"Information is given in manual",29]
[null,"4x0001",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0002",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0003",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0004",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0005",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0006",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0007",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0008","A1 T AUTO","R","R/W","int16",50,650,5,65,"*10","°C",null,"Information is given in manual",30]
[null,"4x0009","A2 T ECO","R","R/W","int16",50,550,5,55,"*10","°C",null,"Information is given in manual",30]
[null,"4x0010","A3 T BOOST","R","R/W","int16",50,650,5,65,"*10","°C",null,"Information is given in manual",30]
[null,"4x0011",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0012",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0013",null,"R","R/W","uint16",0,2,0,2,"*1"," "]
[null,"4x0014","B01 Source flow control (0=AUTO 1=FIXED 2=DELTA T 3=RETURN T)","R","R/W","uint16",0,3,0,3,"*1"," ",null,"Information is given in manual",31]
[null,"4x0015","B02 Low tariff (0=OFF, 1=Standart,2=EL optimal 1, 3=EL optimal 2)","R","R/W","uint16",0,3,0,3,"*1"," ",null,"Information is given in manual",32]
[null,"4x0016","B03 Hot on time","R","R/W","uint16",0,30,0,30,"*1","Days",null,"Information is given in manual",32]
[null,"4x0017","B05 PV (0=OFF, 1=ECO, 2=STORAGE)","R","R/W","uint16",0,2,0,2,"*1"," ",null,"Information is given in manual",32]
[null,"4x0018",null,"R","R/W","uint16",0,1,0,1,"*1","ON/OFF"]
[null,"4x0019",null,"R","R/W","uint16",0,1,0,1,"*1","ON/OFF"]
[null,"4x0020",null,"R","R/W","uint16",50,500,5,50,"*10","°C"]
[null,"4x0021",null,"R","R/W","uint16",0,1,0,1,"*1","ON/OFF"]
[null,"4x0022",null,"R","R/W","uint16",100,300,10,30,"*10","°C"]
[null,"4x0023",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0024",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0025","C0 Reset (1=RESET)","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",33]
[null,"4x0026","C1.1 Model","R","R","uint16",0,65535,0,65535,"*1","Seconds",null,"Information is given in manual",33]
[null,"4x0027","C1.2 Software","R","R","uint16",0,65530,0,6553,"*10","Seconds",null,"Information is given in manual",33]
[null,"4x0028",null,"R","R/W","uint16",0,65535,0,65535,"*1"," "]
[null,"4x0029","C2.1 Hour","R","R/W","uint16",0,23,0,23,"*1","Hours",null,"Information is given in manual",33]
[null,"4x0030","C2.2 Minutes","R","R/W","uint16",0,59,0,59,"*1","Minuten",null,"Information is given in manual",33]
[null,"4x0031","C3.1 Date","R","R/W","uint16",0,31,0,31,"*1"," ",null,"Information is given in manual",33]
[null,"4x0032","C3.2 Month","R","R/W","uint16",1,12,1,12,"*1"," ",null,"Information is given in manual",33]
[null,"4x0033","C3.3 Year","R","R/W","uint16",0,99,0,99,"*1"," ",null,"Information is given in manual",33]
[null,"4x0034","C4 Day","R","R/W","uint16",1,7,1,7,"*1","ON/OFF",null,"Information is given in manual",33]
[null,"4x0035","C5 Language (0=UK, 1=DE, 2=FR, 3=DK, 4=NL, 5=PL, 6=ITA)","R","R/W","uint16",0,6,0,6,"*1"," ",null,"Information is given in manual",33]
[null,"4x0036","C6 Contrast","R","R/W","uint16",0,8,0,8,"*1"," ",null,"Information is given in manual",33]
[null,"4x0037"," ","R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0038","D0 Reset All (1=RESET)","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",34]
[null,"4x0039","D02.1 Modbus address","R","R/W","uint16",1,247,1,247,"*1"," ",null,"Information is given in manual",34]
[null,"4x0040","D02.2 Modbus baud rate (0=9600 , 1 = 19200)","R","R/W","uint16",0,1,0,1,"*1"," ",null,"Information is given in manual",34]
[null,"4x0041","D02.3 Modbus parity (0 = NONE, 1 = EVEN, 2 = ODD)","R","R/W","uint16",0,2,0,2,"*1"," ",null,"Information is given in manual",34]
[null,"4x0042","D02.4 Modbus modify (0=Write disabled)","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",34]
[null,"4x0043","D03 Source flow max","R","R/W","uint16",0,100,0,100,"*1","%",null,"Information is given in manual",34]
[null,"4x0044","D04 Source flow min","R","R/W","uint16",0,100,0,100,"*1","%",null,"Information is given in manual",34]
[null,"4x0045","D05 DELTA T Source","R","R/W","int16",-200,200,-20,20,"*10","°C",null,"Information is given in manual",34]
[null,"4x0046","D06 Return T","R","R/W","int16",-200,500,-20,50,"*10","°C",null,"Information is given in manual",34]
[null,"4x0047","D07 Source T min","R","R/W","int16",-150,300,-15,30,"*10","°C",null,"Information is given in manual",35]
[null,"4x0048","D08 Source T max","R","R/W","int16",200,890,20,89,"*10","°C",null,"Information is given in manual",35]
[null,"4x0049","D09 Water T max","R","R/W","int16",500,700,50,70,"*10","°C",null,"Information is given in manual",35]
[null,"4x0050","D10 Evaporator T max","R","R/W","int16",200,600,20,60,"*10","°C",null,"Information is given in manual",35]
[null,"4x0051","D11 Evaporator T min","R","R/W","int16",-200,200,-20,20,"*10","°C",null,"Information is given in manual",35]
[null,"4x0052","D12 Backup T","R","R/W","int16",50,650,5,65,"*10","°C",null,"Information is given in manual",35]
[null,"4x0053","D13 Legionella (1=ON)","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",35]
[null,"4x0054","D14 Legionella T","R","R/W","int16",550,650,55,65,"*10","°C",null,"Information is given in manual",35]
[null,"4x0055","D15 Legionella day (1 = Monday 2=Tuesday .. etc.)","R","R/W","uint16",1,7,1,7,"*1","Days",null,"Information is given in manual",35]
[null,"4x0056","D16 Forced operation (1=ON)","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",36]
[null,"4x0057","D17.1 Low tariff week-day start hour#1 (-1 = OFF)","R","R/W","int16",-1,23,-1,23,"*1"," ",null,"Information is given in manual",36]
[null,"4x0058","D17.2 Low tariff week-day end hour#1","R","R/W","int16",0,23,0,23,"*1"," ",null,"Information is given in manual",36]
[null,"4x0059","D17.3 Low tariff week-day start hour#2 (-1 = OFF)","R","R/W","int16",-1,23,-1,23,"*1"," ",null,"Information is given in manual",36]
[null,"4x0060","D17.4 Low tariff week-day end hour#2","R","R/W","int16",0,23,0,23,"*1"," ",null,"Information is given in manual",36]
[null,"4x0061","D17.5 Low tariff week-day start hour#3 (-1 = OFF)","R","R/W","int16",-1,23,-1,23,"*1"," ",null,"Information is given in manual",36]
[null,"4x0062","D17.6 Low tariff week-day end hour#3","R","R/W","int16",0,23,0,23,"*1"," ",null,"Information is given in manual",36]
[null,"4x0063","D18.1 Low tariff week-end start hour#1 (-1 = OFF)","R","R/W","int16",-1,23,-1,23,"*1"," ",null,"Information is given in manual",36]
[null,"4x0064","D18.2 Low tariff week-end end hour#1","R","R/W","int16",0,23,0,23,"*1"," ",null,"Information is given in manual",36]
[null,"4x0065","D18.3 Low tariff week-end start hour#2 (-1 = OFF)","R","R/W","int16",-1,23,-1,23,"*1"," ",null,"Information is given in manual",36]
[null,"4x0066","D18.4 Low tariff week-end end hour#2","R","R/W","int16",0,23,0,23,"*1"," ",null,"Information is given in manual",36]
[null,"4x0067","D18.5 Low tariff week-end start hour#3 (-1 = OFF)","R","R/W","int16",-1,23,-1,23,"*1"," ",null,"Information is given in manual",36]
[null,"4x0068","D18.6 Low tariff week-end end hour#3","R","R/W","int16",0,23,0,23,"*1"," ",null,"Information is given in manual",36]
[null,"4x0069","D19 Daylight Saving Time(1=ON)","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",36]
[null,"4x0070","D20 PV min voltage HP","R","R/W","uint16",0,100,0,10,"*10","Volt",null,"Information is given in manual",36]
[null,"4x0071","D21 PV min voltage EL","R","R/W","uint16",0,100,0,10,"*10","Volt",null,"Information is given in manual",36]
[null,"4x0072","D22 PV min time","R","R/W","uint16",0,99,0,99,"*1","Minuten",null,"Information is given in manual",36]
[null,"4x0073","D23 SG ready (1=ON)","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",37]
[null,"4x0074","D24 External control (0=OFF, 1=Start/Stop)","R","R/W","uint16",0,1,0,1,"*1"," ",null,"Information is given in manual",37]
[null,"4x0075","D25 Service timer (0=OFF 1=ON)","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",37]
[null,"4x0076","D26 Service interval","R","R/W","uint16",0,36,0,36,"*1","Months",null,"Information is given in manual",37]
[null,"4x0077","D27 Service reset","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",37]
[null,"4x0078","D28 T HP Max","R","R/W","int16",550,700,55,70,"*10","°C",null,"Information is given in manual",37]
[null,"4x0079",null,"R","R/W","uint16",0,1,0,1,"*1","ON/OFF"]
[null,"4x0080","D29 Demo Mode","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",37]
[null,"4x0081","D30 Preheat hysteresis","R","R/W","int16",-200,200,-20,20,"*10","°C",null,"Information is given in manual",37]
[null,"4x0082","D31 Preheat (Coil)","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",37]
[null,"4x0083","D32 Interim (Coil + HP)","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",38]
[null,"4x0084","D33 Pump / Valve (0 = Valve, 1=Pump)","R","R/W","uint16",0,1,0,1,"*1"," ",null,"Information is given in manual",38]
[null,"4x0085","D34 Water hysteresis ","R","R/W","int16",10,200,1,20,"*10","°C",null,"Information is given in manual",38]
[null,"4x0086","D35 Brine (0=OFF 1=ON)","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Information is given in manual",38]
[null,"4x0087",null,"R","R/W","uint16",0,0,0,0,"*1"," ",null,"Information is given in manual",38]
[null,"4x0088",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0089","M01 Time flow increase","R","R/W","uint16",0,120,0,120,"*1","Seconds",null,"Only for development"]
[null,"4x0090","M02 Time flow decrease","R","R/W","uint16",0,120,0,120,"*1","Seconds",null,"Only for development"]
[null,"4x0091","M04 Auxiliary Pump","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Only for development"]
[null,"4x0092","M03 DELTA T preheat","R","R/W","int16",0,500,0,50,"*10","°C",null,"Only for development"]
[null,"4x0093","M05 Password","R","R/W","uint16",0,9999,0,9999,"*1"," ",null,"Only for development"]
[null,"4x0094","M06 Reset Event Log","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Only for development"]
[null,"4x0095","M07 Save Restore Setpoints (1=RestoreFromBackup, 2=SaveToBackup, 3=RestoreFirstTimeReset) ","R","R/W","uint16",0,3,0,3,"*1"," ",null,"Only for development"]
[null,"4x0096","M08 PVT Booster","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Only for development"]
[null,"4x0097","M09 External Pump","R","R/W","uint16",0,1,0,1,"*1","ON/OFF",null,"Enable/disable external pump operation, only on Microboosters with valve and no coil (V)"]
[null,"4x0098",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0099",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0100","I08 HP MWHe","R","R/W","uint16",0,6553500,0,65535,"*100"," ",null,"Information is given in manual",27]
[null,"4x0101","I10 HP MWHt","R","R/W","uint16",0,6553500,0,65535,"*100"," ",null,"Information is given in manual",27]
[null,"4x0102","I11 EL MWHe","R","R/W","uint16",0,6553500,0,65535,"*100"," ",null,"Information is given in manual",27]
[null,"4x0103","I06 Start/Stops ","R","R/W","uint16",0,65535,0,65535,"*1"," ",null,"Information is given in manual",27]
[null,"4x0104","I01 HP Hours (2 hours)","R","R/W","uint16",0,65535,0,65535,"*1"," ",null,"Information is given in manual",27]
[null,"4x0105","I02 EL Hours (2 hours)","R","R/W","uint16",0,65535,0,65535,"*1"," ",null,"Information is given in manual",27]
[null,"4x0106","I03 Flow Hours (2 hours)","R","R/W","uint16",0,65535,0,65535,"*1"," ",null,"Information is given in manual",27]
[null,"4x0107","BaclupModeRestTime (2 hours)","R","R/W","uint16",0,65535,0,65535,"*1"," ",null,"Only for development"]
[null,"4x0108","HotOnRestTime (2 hours)","R","R/W","uint16",0,65535,0,65535,"*1"," ",null,"Only for development"]
[null,"4x0109","PowerOnCount","R","R/W","uint16",0,65535,0,65535,"*1"," ",null,"Only for development"]
[null,"4x0110","Backup Mode On Time (2 hours)","R","R/W","uint16",0,65535,0,65535,"*1"," ",null,"Only for development"]
[null,"4x0111","Service (2 hours)","R","R/W","uint16",0,65535,0,65535,"*1"," ",null,"Information is given in manual",28]
[null,"4x0112",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0113",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0114",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0115","Last Legionelle Date Month","R","R/W","uint16",0,65535,0,65535,"*1"," ",null,"Only for development"]
[null,"4x0116",null,"R","R/W","uint16",0,0,0,0,"*1"," "]
[null,"4x0117","Restart Unit (0=OFF 1=ON)","R","R/W","uint16",1,1,1,1,"*1","ON/OFF",null,"Only for development"]
[null,"4x0118",null,"R","R/W","uint16",0,65535,0,65535,"*1"," "]
[null,"4x0119",null,"R","R/W","uint16",0,65535,0,65535,"*1"," "]
[null,"4x0120","ErrNoCapacityCnt",null,null,null,null,null,null,null,null,null,null,"Display error value"]
[null,"4x0121"]
[null,"4x0122","ErrNoCapacityCntDwn1",null,null,null,null,null,null,null,null,null,null,"No capacity counter, -1 every hour"]
[null,"4x0123","ErrNoCapacityCntDwn2",null,null,null,null,null,null,null,null,null,null,"No capacity counter, -1 every hour"]
[null,"4x0124"]
[null,"4x0125"]
[null,"4x0126","T1_ErrorCnt",null,null,null,null,null,null,null,null,null,null,"Display error value"]
[null,"4x0127","T2_ErrorCnt",null,null,null,null,null,null,null,null,null,null,"Display error value"]
[null,"4x0128","T3_ErrorCnt",null,null,null,null,null,null,null,null,null,null,"Display error value"]
[null,"4x0129","T4_ErrorCnt",null,null,null,null,null,null,null,null,null,null,"Display error value"]
[null,"4x0130","T5_ErrorCnt",null,null,null,null,null,null,null,null,null,null,"Display error value"]
[null,"4x0131","RressorstatErrorCnt",null,null,null,null,null,null,null,null,null,null,"Display error value"]
[null,"4x0132","HotEvapErrorCnt",null,null,null,null,null,null,null,null,null,null,"Display error value"]
[null,"4x0133","ColdEvapErrorCnt",null,null,null,null,null,null,null,null,null,null,"Display error value"]
[null,"4x0134","HotSourceErrorCnt",null,null,null,null,null,null,null,null,null,null,"Display error value"]
[null,"4x0135"]
[null,"4x0136"]
[null,"4x0137"]
[null,"4x0138"]
[null,"4x0139"]
[null,"4x0140"]
[null,"4x0141"]
[null,"4x0142"]
[null,"4x0143"]
[null,"4x0144"]
[null,"4x0145"]
[null,"4x0146"]
[null,"4x0147"]
[null,"4x0148"]
[null,"4x0149"]

{"sheet":"Datapoint (input)","index":1,"n_rows":124,"n_cols":9,"rows_kept":124,"cut":false,"hidden":false,"merged":[]}
[]
[null,"Modbus datapoints P631","Input register","Microbooster\nFirmware 1.5\n20-05-2021"]
[]
[null,"Modbus Code","Parameter","Data Type","Format","Unit",null,"Comment","Page in manual"]
[null,"3x0000","ADCvalueCH2","uint16","*1"," ",null,"Only for development"]
[null,"3x0001","ADCvalueCH3","uint16","*1"," ",null,"Only for development"]
[null,"3x0002","ADCvalueCH4","uint16","*1"," ",null,"Only for development"]
[null,"3x0003","ADCvalueCH7","uint16","*1"," ",null,"Only for development"]
[null,"3x0004","ADCvalueCH10","uint16","*1"," ",null,"Only for development"]
[null,"3x0005","ADCvalueCH11","uint16","*1"," ",null,"Only for development"]
[null,"3x0006","ADCvalueCH12","uint16","*1"," ",null,"Only for development"]
[null,"3x0007","ADCvalueCH13","uint16","*1"," ",null,"Only for development"]
[null,"3x0008","ADCvalueCH14","uint16","*1"," ",null,"Only for development"]
[null,"3x0009","ADCvalueCH15","uint16","*1"," ",null,"Only for development"]
[null,"3x0010",null,null,null," "]
[null,"3x0011","T1 T source in","int16","*10","°C",null,"Information is given in manual",27]
[null,"3x0012","T2 T source out","int16","*10","°C",null,"Information is given in manual",27]
[null,"3x0013","T3 T tank","int16","*10","°C",null,"Information is given in manual",27]
[null,"3x0014","T4","int16","*10","°C",null,"Not used on Microbooster"]
[null,"3x0015","T5","int16","*10","°C",null,"Not used on Microbooster"]
[null,"3x0016","Coil",null,null,"ON/OFF",null,"Only for development"]
[null,"3x0017","Microbooster Mode","uint16","*1"," ",null,"Information is given in manual","28/29"]
[null,"3x0018","ExternalPump","uint16","*1","ON/OFF",null,"Only for development"]
[null,"3x0019","R1 Flow ON","uint16","*1","ON/OFF",null,"Information is given in manual",27]
[null,"3x0020","R2 Flow OFF","uint16","*1","ON/OFF",null,"Information is given in manual",27]
[null,"3x0021","R3 Coil / External Pump","uint16","*1","ON/OFF",null,"Information is given in manual",27]
[null,"3x0022","R4 HP","uint16","*1","ON/OFF",null,"Information is given in manual",27]
[null,"3x0023","R5 El Heater","uint16","*1","ON/OFF",null,"Information is given in manual",27]
[null,"3x0024","R6 Pressostat","uint16","*1","ON/OFF",null,"Information is given in manual",27]
[null,"3x0025","SG1 input","uint16","*1","ON/OFF",null,"Information is given in manual",27]
[null,"3x0026","SG2 input","uint16","*1","ON/OFF",null,"Information is given in manual",27]
[null,"3x0027","Input V","uint16","*10","Volt",null,"Information is given in manual",27]
[null,"3x0028","T avg source in","int16","*10","°C",null,"Information is given in manual",27]
[null,"3x0029","T avg source out","int16","*10","°C",null,"Information is given in manual",27]
[null,"3x0030","El Power","uint16","*100"," ",null,"Information is given in manual",27]
[null,"3x0031","W el total","uint16","*100"," ",null,"Information is given in manual",27]
[null,"3x0032","Heating C","uint16","*100"," ",null,"Information is given in manual",27]
[null,"3x0033","Water P","uint16","*100"," ",null,"Information is given in manual",27]
[null,"3x0034",null,null,null," "]
[null,"3x0035","T1 Error","uint16","*1","ON/OFF",null,"Information is given in manual",28]
[null,"3x0036","T2 Error","uint16","*1","ON/OFF",null,"Information is given in manual",28]
[null,"3x0037","T3 Error","uint16","*1","ON/OFF",null,"Information is given in manual",28]
[null,"3x0038","T4 Error","uint16","*1","ON/OFF",null,"Information is given in manual",28]
[null,"3x0039","T5 Error","uint16","*1","ON/OFF",null,"Information is given in manual",28]
[null,"3x0040","HP Error","uint16","*1","ON/OFF",null,"Information is given in manual",28]
[null,"3x0041","Hot Evap Error","uint16","*1","ON/OFF",null,"Information is given in manual",28]
[null,"3x0042","Cold Evap Error","uint16","*1","ON/OFF",null,"Information is given in manual",28]
[null,"3x0043","ModBusError","uint16","*1","ON/OFF",null,"Information is given in manual",28]
[null,"3x0044","ServiceError","uint16","*1","ON/OFF",null,"Information is given in manual",28]
[null,"3x0045","No Capacity Error","uint16","*1","ON/OFF",null,"Information is given in manual",28]
[null,"3x0046","Hot Source T Error","uint16","*1","ON/OFF",null,"Information is given in manual",28]
[null,"3x0047"]
[null,"3x0048","HP_OnTemp","int16","*10","°C",null,"Temperature to turn on HP"]
[null,"3x0049","HP_OffTemp","int16","*10","°C",null,"Temperature to turn off HP"]
[null,"3x0050","HP_Released","uint16","*1","ON/OFF",null,"Is HP enabled?"]
[null,"3x0051","E_HeatOnTemp","int16","*10","°C",null,"Temperature to turn on heating element"]
[null,"3x0052","E_HeatOffTemp","int16","*10","°C",null,"Temperature to turn off heating element"]
[null,"3x0053","E_HeatReleasedLevel","uint16","*1","ON/OFF",null,"Is heating element enabled?"]
[null,"3x0054","Cold Mode On","uint16","*1","ON/OFF",null,"Only for development"]
[null,"3x0055","Hot Mode On","uint16","*1","ON/OFF",null,"Only for development"]
[null,"3x0056","HotSourceErrorCnt1","uint16","*1"," ",null,"Hot source error count 1, first time within a week"]
[null,"3x0057","HotSourceErrorCnt2","uint16","*1"," ",null,"Hot source error count 2, second time within a week"]
[null,"3x0058","HotSourceErrorCnt3","uint16","*1"," ",null,"Hot source error count 3, third time within a week"]
[null,"3x0059","Compressor State","uint16","*1"," ",null,"Only for development"]
[null,"3x0060","WP_StateTimer","uint16","*1","Seconds",null,"Only for development"]
[null,"3x0061","Source In Last Run","int16","*10","°C",null,"Source in last run"]
[null,"3x0062","CompressorOnTime","uint16","*1","Seconds",null,"Compressor on time"]
[null,"3x0063","Compressor Pause Cnt","uint16","*1","Seconds",null,"Compressor pause counter"]
[null,"3x0064","Mischer position","uint16","*1"," ",null,"Only for development"]
[null,"3x0065","Mischer counter","uint16","*1","Seconds",null,"Only for development"]
[null,"3x0066","E74_Delta_T_water","int16","*10","°C",null,"Flow handling"]
[null,"3x0067","E75_Delta_T_water","int16","*10","°C",null,"Flow handling"]
[null,"3x0068","Flow %","uint16","*1","%",null,"Flow percentage"]
[null,"3x0069","R5_ElHeaterOld","uint16","*1","ON/OFF",null,"Only for development"]
[null,"3x0070","HP_ON","uint16","*1"," ",null,"Heat production present"]
[null,"3x0071",null,null,null," "]
[null,"3x0072","HP_Hours_Sec","uint16","*1","Seconds",null,"HP time in seconds"]
[null,"3x0073","EL_Hours_Sec","uint16","*1","Seconds",null,"heating element time in secounds"]
[null,"3x0074","FlowHours_Sec","uint16","*1"," ",null,"Flow time in seconds"]
[null,"3x0075","BaclupModeRestTime_Sec","uint16","*1","Seconds",null,"Only for development"]
[null,"3x0076","HotOnRestTime_Sec","uint16","*1","Seconds",null,"Only for development"]
[null,"3x0077","BackUpModeOnTime_Sec","uint16","*1","Seconds",null,"Only for development"]
[null,"3x0078","FilterOnTime_Sec","uint16","*1","Seconds",null,"Only for development"]
[null,"3x0079",null,null,null," "]
[null,"3x0080",null,null,null," "]
[null,"3x0081","T1_ErrorCnt","uint16","*1","Seconds",null,"T1 error count"]
[null,"3x0082","T2_ErrorCnt","uint16","*1","Seconds",null,"T2 error count"]
[null,"3x0083","T3_ErrorCnt","uint16","*1","Seconds",null,"T3 error count"]
[null,"3x0084","T4_ErrorCnt","uint16","*1","Seconds",null,"T4 error count"]
[null,"3x0085","T5_ErrorCnt","uint16","*1","Seconds",null,"T5 error count"]
[null,"3x0086","RressorstatErrorCnt","uint16","*1","Seconds",null,"Pressostat error count"]
[null,"3x0087","HotEvapErrorCnt","uint16","*1","Seconds",null,"Hot evaporator error count"]
[null,"3x0088","ColdEvapErrorCnt1","uint16","*1","Seconds",null,"Cold evaporator error count 1, first time within a week"]
[null,"3x0089","ModBusErrorCnt","uint16","*1","Seconds",null,"ModBus error count"]
[null,"3x0090","NoCapacityErrorCnt","uint16","*1"," ",null,"No capacity error count"]
[null,"3x0091","ColdEvapErrorCnt2","uint16","*1"," ",null,"Cold evaporator error count 2, second time within a week"]
[null,"3x0092","BackUpAnswer","uint16","*1"," ",null,"Allow electrical heating element to continue operation"]
[null,"3x0093","Errors","uint16","*1","Binary",null,"T1_Error                                                                     Bit0\nT2_Error                                                                     Bit1\nT3_Error                                                                     Bit2\nHP_Error                                                                     Bit5\nColdEvapError                                                          Bit6\nHotEvapError                                                           Bit7\nNoCapacityError                                                      Bit8\nHotSourceTempError                                            Bit9\nServiceError                                                               Bit10\nModBusError                                                           Bit15\nNoCapacityKompressorPause                            Bit13\nNoCapacitySwitchToEheater                              Bit14"]
[null,"3x0094","ColdEvapErrorCnt3","uint16","*1"," ",null,"Cold evaporator error count 3, third time within a week"]
[null,"3x0095","T3_TtankOld","int16","*10"," ",null,"Only for development"]
[null,"3x0096","Optimal Release HP","uint16","*1"," ",null,"Only for development"]
[null,"3x0097","Optimal EL ON","uint16","*1"," ",null,"Only for development"]
[null,"3x0098","Legionella State","uint16","*1"," ",null,"Legionella signal"]
[null,"3x0099","Low Tarif OnOff","uint16","*1"," ",null,"Low tarif signal"]
[null,"3x0100","PV State","uint16","*1","Binary",null,"PV signal"]
[null,"3x0101","SG state","uint16","*1"," ",null,"SG signal"]
[null,"3x0102",null,null,null," "]
[null,"3x0103","Extern Control State","uint16","*1"," ",null,"External control"]
[null,"3x0104",null,null,null," "]
[null,"3x0105","Power Fan","uint16","*1"," ",null,"Fan power estimate"]
[null,"3x0106","Power Compressor ","uint16","*1"," ",null,"Compressor power estimate"]
[null,"3x0107","HPWe (Compressor + Fan)","uint16","*1"," ",null,"HP power estimate"]
[null,"3x0108","Optimal Qdisp/(Vn*dw*cw)","int16","*10"," ",null,"Only for development"]
[null,"3x0109","Optimal Qreq/(Vn*dw*cw)","int16","*10"," ",null,"Only for development"]
[null,"3x0110",null,null,null," "]
[null,"3x0111",null,null,null," "]
[null,"3x0112",null,null,null," "]
[null,"3x0113",null,null,null," "]
[null,"3x0114",null,null,null," "]
[null,"3x0115",null,null,null," "]
[null,"3x0116","PassWordOKcntDown","uint16","*1","Seconds",null,"Password OK countdown"]
[null,"3x0117",null,null,null," "]
[null,"3x0118",null,null,null," "]
[null,"3x0119",null,null,null," "]